## QA PROMPTS v1.0
QA PROMPTS v1.0
No. | QA Prompt | PD | SD | DD | CD
A-101 OVERALL FLOOR PLANS
1 | CONFIRM IF YOUR PROJECT WILL HAVE A COMBINED FLOOR PLAN WITH ANNOTATION AND DIMENSIONS OR IF THERE WILL BE A SEPARATE DIMENSION PLAN | NA | NA
2 | EDIT NON-APPLICABLE GENERAL NOTES | NA
3 | SHOW THE ARCHITECTURAL LIMIT
4 | PROVIDE KEY PLAN | NA | NA
5 | TAG ALL WALL TYPES | NA | NA
6 | TAG ALL DOORS | OPENINGS | WINDOWS (INCLUDE RATING WHERE APPLICABLE) | NA | NA
7 | COORDINATE OPENINGS WITH FRAMES AND GLAZING TYPES | NA | NA
8 | SHOW DIMENSIONS IN THIS PLAN IF NO DIMENSION PLAN IS INCLUDED - ALL ROOMS PER PRACTICE AREA BEST METHODS PER PM: FINISHED FACE TO FINISHED FACE / COLUMN TO GRID LINE | NA | NA
9 | IDENTIFY ENLARGED PLAN AREAS | NA | NA
10 | CHECK WALL TYPES FOR RATED | COLUMN ENCLOSURES | PLUMBING PIPES ARE SIZED CORRECT | NA
11 | ENSURE ALL DISCIPLINES ARE WORKING FROM THE MOST CURRENT BACKGROUNDS | NA
12 | ALL ROOMS AND ROOM NUMBERS TO BE TAGGED | NA | NA
13 | INCLUDE KEY PLAN FOR LARGE FACILITIES OR DIVIDED AREA PLANS | NA
14 | ALL CALL-OUT AREA INFORMATION TO BE LOCATED IN ENLARGED DETAILS / PLANS. FLOOR PLAN TO ONLY SHOW THE CALL-OUT TAG | NA
15 | REVIEW CORRIDOR WIDTHS FOR CLEAR WIDTH REQUIRED PER CODE AND FOR EQUIPMENT RIGGING | NA
16 | ENSURE ALL WALL SECTIONS | CALL-OUTS | ELEVATION MARKERS ARE SHOWING ON THE PLANS | NA | NA
17 | ENSURE THE DOOR SWINGS ARE ALIGNED WITH THE LIFESAFETY PLANS | NA
18 | CONFIRM THE DIMENSION MARGIN IS SET TO MIN 1/8" | NA
19 | ENSURE THE GENERAL NOTES FOR DIMENSIONING INDICATE YOUR STRATEGY FOR DIMENSIONING. | NA | NA
20 | ALL PLUMBING FIXTURES SHOULD SHOW IN THE PLAN | NA
21 | AT ALL MATCHLINES | TAG MATCHING PLAN | NA
22 | INDICATE SLOPE AT AREA OF SLOPED FLOOR | NA
23 | SHOW FRT PLYWOOD AT IT WALLS AND ELECTRICAL CLOSETS | NA | NA
24 | REVIEW TRAVEL PATHS FOR LARGE EQUIPMENT WITH PM | NA
25 | CHECK DOOR SWING DIRECTIONS WITH PM FOR EGRESS | NA | NA
26 | CHECK DOOR SWING DIRECTIONS WITH PM AT TOILETS | NA
A-101a AREA PLANS (ANNOTATION or DIMENSION)
1 | REVIEW MARGIN OF ERROR ACCEPTABLE INDUSTRY STANDARDS FOR DIMENSIONS WITH PM | NA
2 | FOR NEW CONSTRUCTION PROJECTS SHOW DIMENSIONS FROM COLUMN GRIDS | NA
3 | FOR RENOVATION BUILDING PROJECTS SHOW DIMENSIONS FROM EXTERIOR WALLS | STAIR TOWERS | ELEVATOR SHAFTS ( KNOWN POINTS) | NA
4 | FOR INTERIOR RENOVATION PROJECT SHOW DIMENSIONS FROM FINISHED FACE TO FINISHED FACE OF INTERIOR WALLS. | NA
5 | USE HOLD / MIN /MAX DIMENSIONS FOR PRIORITY SPACES TO SHOW DESIGN INTENT | NA
6 | ENSURE DIMENSION LOCATIONS ARE LEGIBLE | NA
7 | INDICATE DRAWING SCALE | NA
A-141 OVERALL RCP PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA
2 | COMPARE GENERAL NOTES WITH MEP GENERAL NOTES AND ADJUST CONFLICTING NOTES | NA | NA
3 | SHOW THE ARCHITECTURAL LIMIT
4 | CONFIRM CEILINGS ARE CENTERED TO THE ROOM | NA
5 | CONFIRM LIGHT FIXTURE TYPES ARE COORDINATED WITH MEP DRAWINGS | NA | NA
6 | DIMENSION ALL LIGHT LOCATIONS AT GYPSUM CEILINGS | NA | NA
7 | CONFIRM ALL CEILING MOUNTED EQUIPMENT IS COORDINATED WITH MEP DRAWINGS AND AV DRAWINGS | NA | NA
8 | COORDINATE HVAC SUPPLY/ RETURN DIFFUSERS | EXHAUST WITH MECHANCAL DRAWINGS | NA | NA
9 | SHOW PLENUM SECTION WITH CEILING | STRUCTURE | LIGHT FIXTURE HOUSING | DUCTS | SLAB HEIGHTS IN INTERNAL COORDINATION VIEW | NA | NA
10 | KEY IN REFERENCES OR NOTE REFERENCES TO BULKHEAD/SOFFIT SECTIONS | NA | NA
11 | CHECK GRAPHIC STANDARDS SO CEILING MATERIAL HATCHES AND CEILING ELEMENTS MATCH LEGEND | NA | NA
12 | INDICATE CEILING HEIGHT AND CEILING TYPE IN EVERY ROOM | NA
13 | SHOW DOOR HEADERS; AVOID SHOWING DOOR SWINGS | NA | NA
14 | INDICATE DRAWING SCALE | NA
A-141a RCP AREA PLANS
1 | IF AREA PLANS ARE CREATED | MAKE SURE ALL DETAILS ARE SHOWING IN AREA PLANS AND NOT ON THE OVERALL REFLECTED CElLING PLAN | NA
2 | ARRANGE PLANS TO FIT SHEET SIZE; ARRANGE AND TAG MATCHLINES | NA
A-151 ROOF PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA
2 | SHOW THE ARCHITECTURAL LIMIT
3 | DIMENSION/TAG ROOF PEAKS | VALLEYS | CRICKETS | GUTTERS | DRAINS IN PLAN AND SECTION | NA | NA | NA
4 | SHOW MEP EQUIPMENT | NA | NA
5 | INDICATE ROOF SLOPE | NA | NA
6 | SHOW ROOF ASSEMBLY TYPE AND REFERENCE DETAIL | NA | NA | NA
7 | SHOW LADDER LOCATION AND REFERENCE DETAILS | NA | NA
8 | SHOW PARAPET HEIGHT AND COPING AND REFERENCE DETAILS | NA | NA
9 | SHOW ROOF ACCESS AND CLIENT REQUIRED ROOF HATCH/LADDER AND REFERENCE DETAILS | NA | NA
10 | SHOW WALKWAY PROTECTION PATHS AND REFERENCE DETAILS | NA | NA
11 | SHOW EQUIPMENT SCREENING AND REFERENCE DETAILS | NA | NA
12 | REFERENCE ROOFING COMPONENT DETAILS | NA | NA
13 | KEY IN WALL/ROOF ASSEMBLY SECTION MARKERS | NA | NA
14 | INDICATE DRAWING SCALE | NA
A-161 SOUND TRANSMISSION PLANS
1 | SHOW THE ARCHITECTURAL LIMIT | NA
2 | IDENTIFY AHJ REQUIRED STC RATINGS AND NOTE ON PARTITION TYPES | NA | NA
3 | CHECK ALL FULL HEIGHT STC RATED PARTITIONS ARE LOCATED AT REQUIRED LOCATIONS; CHECK MECHANICAL DUCT PENETRATIONS FOR SOUND TRANSFER MITIGATION STRATEGIES | NA | NA | NA
4 | CHECK DOOR/DOOR FRAME ASSEMBLIES ARE COORDINATED WITH THEIR ADJACENT WALL ASSEMBLIES FOR REQUIRED STC RATINGS | NA | NA
5 | CHECK NOISE REDUCTION COEFFICIENT RATING FOR ROOM FINISHES MEET CLIENT GOALS | NA | NA | NA
6 | INDICATE DRAWING SCALE | NA
A-201 BUILDING ELEVATIONS
1 | IDENTIFY AND SHOW COMPLIANCE WITH ZONING REQUIREMENTS ( MATERiALS | HEIGHTS | BUILDING FORM | MATERIALS | RTU SCREENING)
2 | IDENTIFY DESIGN TEAM AESTHETIC/BUILDING FORM GOALS AND SHOW COMPLIANCE | NA
3 | IDENTIFY EXPOSED STEEL | NA | NA
4 | SHOW ALL VISIBLE MEP SCOPE (LOUVERS | DRAINS | ROOF TOP UNITS | LIGHT FIXTURES) | NA | NA
5 | ELEVATE AND TAG ALL OPENINGS AND GLAZING TYPES | NA | NA
6 | LOCATE AND SHOW A DETAIL REFERENCE TO ALL REPRESENTATIVE WALL ASSEMBLY SECTIONS | NA | NA
7 | IDENTIFY /TAG EXTERIOR MATERIALS LEGIBLY | NA
8 | SHOW ELEVATION HEIGHTS INCLUDING FINISH (GROUND) FLOOR | NA
9 | SHOW GRADING CONDITIONS INCLUDINGFINISH GRADE LINE | NA | NA
10 | SHOW CONTROL AND EXPANSION JOINTS AND REFERNCE IN DETAILS | NA | NA
11 | INDICATE DRAWING SCALE | NA
A-301 BUILDING SECTIONS
1 | CONFIRM THE SECTION NAME ALIGNS WITH THE DIRECTION OR LOCATION
2 | ALL CRITICAL BUILDING SECTIONS TO BE INCLUDED TO SHOW THE DIFFERENT LEVELS | UNDER SLAB DEPTH | OVERHEAD | PARAPET | ETC. | NA | NA
3 | LOCATE AND REFERENCE WALL SECTION CALL-OUTS | NA | NA
4 | STRUCTURE | DUCT | LIGHTING SHOULD SHOW IN SECTIONS | NA | NA
5 | SHOW GRADING DIFFERENCE FOR SECTION | IF APPLICABLE | NA | NA
6 | SHOW COLUMN GRIDS AND LEVELS | NA | NA
7 | INDICATE DRAWING SCALE | NA
8 | ENSURE LEVELS ARE COORDINATED/CONSISTENT FOR ALL SECTIONS ( TOP OF FLOOR | TOP OF SLAB | TOP OF ROOF) | NA
9 | DIMENSION PERIMETER EXTERIOR WALL FROM GRID LINES | NA | NA
10 | IDENTIFY ALL ASSEMBLIES FROM THE OUTSIDE IN OR INSIDE OUT AND CREATE CONTINUITY FROM ROOF TO FOUNDATION | NA | NA
11 | REFERENCE WALL SECTIONS AND SECTION DETAILS FOR ENTIRE ENVELOPE | NA | NA
12 | INDICATE STRUCTURAL GRID AND LEVELS IN ALL SECTIONS | NA | NA
13 | COORDINATE AND SHOW GRADE BEAMS | BELOW GRADE STRUCTURAL BEAMS AND PILE CAPS AS NOTED IN STRUCTURAL DRAWINGS. | NA | NA
14 | IN ARCHITECTURAL DRAWINGS | GRAPHICALLY DEPICT CAPILLIARY BARRIERS AND VAPOR RETARDERS AS SHOWN AND COORDINATED WITH STRUCTURAL SCOPE | NA | NA
A-311 WALL SECTIONS
1 | SHOW TYPE DETAILS AND INCLUDE BASIC FLASHING | WATERPROOFING | VAPOR RETARDERS | AIR BARRIERS | SEALANTS | MATERIALS | INSULATION ETC; CREATE CONTINUITY FROM ROOF TO FOUNDATION | NA
2 | SHOW STRUCTURAL SYSTEM AND LOCATE CENTERLINE OF STRUCTURE IN WALL SECTION | NA
3 | IDENTIFY ALL MATERIALS FROM THE OUTSIDE IN OR INSIDE OUT. SHOW THE (4) CONTROL LAYERS FOR THE BUILDING ENCLOSURE: BULK WATER CONTROL (EXTERIOR CLADDING) | AIR INFILTATION CONTROL LAYER (AIR BARRIER) | THERMAL CONTROL LAYER (INSULATION) | AND | NA | NA
4 | LOCATE AND REFERENCE DETAILS FOR ALL EXTERIOR MATERIAL TRANSITION LOCATIONS | NA | NA
5 | REFERENCE WALL SECTION DETAILS AT A LARGER SCALE FOR LEGIBILITY | USING SAME COLOR CODED LINE TYPES | INSIDE OUT OR OUTSIDE IN TAGGING AND COORDINATE PER SPECIFICATION SECTIONS | NA | NA
6 | INDICATE DRAWING SCALE | NA
A-401 VERTICAL CIRCULATION
1 | DEVELOP ENLARGED PLANS TO DELINIATE IN MORE DETAIL | COMPARE WITH CODE REQUIREMENT AND CLIENTS NEEDS | NA
2 | FOR ELEVATORS | CONFIRM PIT HEIGHT | OVERHEAD CLEARANCE | AND HOIST CLEAR DIMENSIONS | NA | NA
3 | COORDINATE STRUCTURAL BEAM / COLUMNS ENCLOSURES AND LOCATIONS | NA | NA
4 | DEVELOP STAIR AND ELEVATOR SECTIONS; KEY SECTIONS ON ENLARGED PLANS | NA | NA
5 | DEVELOP DETAILS AND KEY THEM TO PLAN AND SECTIONS | NA | NA
6 | COORDINATE STRUCTURAL OPENINGS AND FRAMING FOR STAIR AND ELEVATOR OPENINGS WITH STRUCTURAL ENGINEER | NA | NA
7 | COORDINATE VENTING AND PRESSURIZATION REQUIREMENTS OF ELEVATOR SHAFTS WITH MEP CONSULTANT | NA | NA
10 | CONFIRM DESIGN INTENT FOR GUARDRAILS AND HANDRAILS IS INDICATED IN THE DETAILS | COMPLY WITH IBC CH 11 OR EQUAL | NA | NA
11 | CONFIRM ADA HEIGHTS ARE SHOWING FOR THE HANDRAILS | NA | NA
12 | SHOW ANY SPECIAL TREATMENT REQUIRED AT LANDING OR AT HEADROOM | NA | NA
13 | INCLUDE ELEVATOR PIT DETAILS | NA | NA
14 | INCLUDE DOG HOUSE DETAIL IF NEEDED FOR THE ELEVATOR OVERRUN | NA | NA
15 | INDICATE DRAWING SCALE | NA
A-501 DETAILS
1 | DETAIL PROJECT SPECIFIC DETAILS | NA | NA
2 | DETAIL ALL NON-TYPICAL CONDITIONS | NA | NA
3 | INDICATE DRAWING SCALE AND ENSURE DRAWING SCALE IS LARGE ENOUGH FOR DETAIL DOCUMENTATION | NA | NA
4 | MAKE REFERENCE TO PLAN DETAILS ON PLANS OR ENLARGED PLANS | NA | NA
5 | SHOW THE NEAREST STRUCTURAL GRID LINE AND TAG | NA | NA
6 | SHOW ASSEMBLY TYPE DETAILS AND INCLUDE BASIC FLASHING | WATERPROOFING | VAPOR RETARDERS | AIR BARRIERS | SEALANTS | MATERIALS | INSULATION ETC; CREATE CONTINUITY FROM ROOF TO FOUNDATION | NA | NA
7 | IDENTIFY ALL MATERIALS FROM THE OUTSIDE IN OR INSIDE OUT. SHOW THE (4) CONTROL LAYERS FOR THE BUILDING ENCLOSURE: BULK WATER CONTROL (EXTERIOR CLADDING) | AIR INFILTATION CONTROL LAYER (AIR BARRIER) | THERMAL CONTROL LAYER (INSULATION) | AND VAPOR CONTROL LAYER ( CLASS 1 | 2 | OR 3). USE COLOR CODED LINETYPES TO DIFFERENTIATE SYSTEMS SUCH AS VAPOR RETARDERS | AIR BARRIERS | FLASHING ETC AND CREATE CONTINUITY FROM ROOF TO FOUNDATION | NA | NA
8 | SHOW CONTINUOUS PATH USING A COLOR LINE TYPE FOR WATER PROOFING MEMBRANES INCLUDING WRAPPING EXTERIOR OPENINGS HEADS | JAMBS | AND UNDER COPINGS | NA | NA
9 | COORDINATE AND DIMENSION EDGE OF SLAB FOR PERIMETER ENLARGED DETAILS | NA | NA
10 | THE PREFERENCE IS TO DRAW DETAILS EVEN IF SIMILAR; DISCUSS THE USE OF SIM /TYP NOTATIONS ON SIMILAR DETAILS WITH YOUR PM | NA | NA
11 | DETAIL RATED WALL AT STRUCTURAL COLUMNS AND ALIGN WITH A UL LISTED DETAIL
AD101 OVERALL DEMOLITION PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA | NA
2 | SHOW THE ARCHITECTURAL / INTERIOR LIMIT - NOT IN SCOPE VS IN SCOPE
3 | SHOW EXISTING ELEMENTS GRAPHICALLY DIFFERENT FROM DEMOLISHED ELEMENTS
4 | REVIEW SCOPE FOR MEP UPDATES (ROOF DRAINS | EXHAUSTS | STRUCTURAL MEMBERS | PLUMBING)
5 | WITH YOUR PM | ANALYZE CODE FOR EACH PHASE AND THE USE OF EXISTING SPACE DURING DEMOLITION
6 | REVIEW NEW WORK FOR ANY CORRESPONDING DEMO SCOPE | NA | NA
7 | SHOW PHASING SCOPE IF ANY | NA | NA
8 | SHOW AN OVERALL DIMENSION FOR PORTIONS OF AN ELEMENT TO BE DEMOLISHED TO HELP THE GC ESTIMATE THE COST FOR DEMOLITION | NA | NA
9 | ARRANGE PLANS TO FIT SHEET SIZE; ARRANGE AND TAG MATCHLINES
10 | SHOW NORTH ARROW
11 | SHOW STRUCTUIRAL GRID | NA | NA
12 | CHECK GRAPHIC STANDARDS FOR HATCHES USED MATCH DEMOLITION LEGEND | NA | NA
13 | INDICATE DRAWING SCALE
AD111 OVERALL CEILING DEMOLITIONS PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA | NA
2 | SHOW THE ARCHITECTURAL LIMIT
3 | COORDINATE ARCH DEMO SCOPE WITH ELECTRICAL | MECHANICAL AND STRUCTURAL DEMO SCOPE | NA | NA | NA
4 | COORDINATE DEMO WORK WITH NEW WORK AREA TO INDICATE THE EXTENT | NA
5 | REVIEW NEW WORK FOR ANY CORRESPONDING DEMO SCOPE | NA
6 | SHOW AN OVERALL DIMENSION FOR PORTIONS OF AN ELEMENT TO BE DEMOLISHED TO HELP THE GC ESTIMATE THE COST FOR DEMOLITION | NA | NA
7 | ARRANGE PLANS TO FIT SHEET SIZE; ARRANGE AND TAG MATCHLINES
8 | SHOW NORTH ARROW
9 | SHOW STRUCTUIRAL GRID | NA
10 | CHECK GRAPHIC STANDARDS FOR HATCHES USED MATCH DEMOLITION LEGEND | NA | NA
11 | INDICATE DRAWING SCALE
AD121 ROOF DEMOLITION PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA | NA
2 | SHOW THE ARCHITECTURAL LIMIT | NA
3 | COORDINATE REMOVAL AND OR OPENINGS FOR FOR EXISTING WORK UPDATE AND NEW INSTALLATIONS | NA
4 | COORDINATE EXISTING ROOF CONSTRUCTION AND NEW CONSTRUCTION TO ANALYZE THE DEMO SCOPE REQUIRED | NA
5 | REVIEW CODE AND ORDINANCES FOR HEIGHT / PARAPET AND SCREEING REQUIREMENTS | NA
6 | ANALYSE GUTTER / ROOF DRAIN / EXHAUST LOCATION CHANGES | NA | NA
7 | SHOW AN OVERALL DIMENSION FOR PORTIONS OF AN ELEMENT TO BE DEMOLISHED TO HELP THE GC ESTIMATE THE COST FOR DEMOLITION | NA | NA
8 | ARRANGE PLANS TO FIT SHEET SIZE; ARRANGE AND TAG MATCHLINES | NA
9 | SHOW NORTH ARROW | NA
10 | SHOW STRUCTUIRAL GRID | NA
11 | CHECK GRAPHIC STANDARDS FOR HATCHES USED MATCH DEMOLITION LEGEND | NA
12 | INDICATE DRAWING SCALE | NA
AS101 ARCHITECTURAL SITE PLAN
1 | EDIT NON-APPLICABLE GENERAL NOTES
2 | DOCUMENT SITE PLAN TO MATCH LEGEND | NA
3 | SHOW AND LABEL EXISTING PLAN VIEW WITH EXISTING CIVIL DRAWINGS (LEVELS | MAIL UTILITY | CONNECTIONS | WALKWAYS | MONUMENTAL SIGNS | MAIN ACCESS); ENSURE EXISTING ITEMS LOOK DIFFERENT COMPARED TO NEW ITEMS | NA
4 | SHOW AND LABEL NEW WORK IN PLAN VIEW WITH CIVIL DRAWINGS (LEVELS | MAIL UTILITY | CONNECTIONS | WALKWAYS | MONUMENTAL SIGNS | MAIN ACCESS) | NA | NA
5 | COORDINATE AND SHOW MONUMENTAL SIGN FOUNDATION DESIGN AND PROVIDE POWER/DATA ETC FOR LIGHTING | NA
6 | SHOW EXISTING AND NEW WORK PLANS VIEW WITH STRUCTURAL DRAWINGS | NA
7 | NOTE PROPERTY DIMENSIONS AND SETBACKS AND EASEMENTS EXPLICITLY | NA
8 | NOTE EXISTING TO REMAIN AND NEW PARKING EXPLICITLY AND SHOW NEW ADA PARKING AS REQUIRED | NA
9 | NOTE DEED RESTRICTIONS EXPLICITLY | NA
10 | NOTE PARKING ORDINANCES FOR OFF STREET PARKING AND LOADING REQUIREMENTS | NA
11 | NOTE SIGNAGE ORDINANCES FOR MONUMENT SIGNAGE | NA | NA
12 | LOCATE AND SHOW ALL EQUIPMENT PADS AND TRANSFORMER PADS AND COORDINATE WITH MEP AND STRUCTURAL (SIZE OF PAD | PSI OF CONCRETE | THICKNESS OF PAD | REBAR | WIRE MESH) | NA | NA
13 | COORDINATE WITH CIVIL ENGINEER AND NOTE FINISHED FLOOR ELEVATION AND NORTH ARROW | NA
14 | SHOW SITE ACCESSIBILITY INCLUDING CURB RAMPS | SLOPES | AND RAILS | NA
15 | SHOW BUILDING UTILITY OUTFLOW LINES | THEIR SIZE AND LOCATIONS | NA | NA
16 | SHOW GUTTER DOWNSPOUTS AND WHERE TIE-INS ARE TO SUB-SURFACE DRAINAGE | NA | NA
17 | SHOW DETAILS FOR ENCLOSURES | SIGNS | FLAGPOLES | FOUNTAINS; FOR NEW FLAGPOLES PROVIDE A FOUNDATION DESIGN AND COORDINATE FOR POWER FOR ANY LIGHTING | NA | NA
18 | SHOW EQUIPMENT CLEAR DIMENSIONS AT ENCLOSURES | NA | NA
19 | NOTE LOCAL ORDINANCE COMPLIANT ENCLOSURE MATERIALS/FINISHES | NA
20 | DESIGNATE ALL ITEMS FOR OWNER/CONTRACTOR FURNISHED/INSTALLED | NA
21 | IDENTIFY METER SIZES IN COMPLIANCE WITH LOCAL MUNICIPALITY FOR DOMESTIC WATER | FIRE AND IRRIGATION LINES | NA | NA
22 | NOTE FIRE LANE REQUIREMENTS | INCLUDING CONFIGURATION AND STRIPING | EXPLICITLY | NA | NA
23 | SHOW MINIIMUM FIRE LANE TURNING RADIUS | NA | NA
24 | SHOW NEW TREE SCOPE AS COORDINATED WITH LANDSCAPE CONSULTANT | NA
25 | SHOW LANDSCAPE IRRIGATION AS COORDINATED WITH LANDSCAPE CONSULTANT | NA
26 | SHOW SLEEVES AT SIDEWALKS AND PAVED AREAS AS COORDINATED WITH LANDSCAPE CONSULTANT | NA
27 | INDICATE DRAWING SCALE | NA
28 | IF WE HAVE A BACKFLOW PREVENTER | LOCATE IT ON THE SITE PLAN AS COORDINATED WITH THE OWNER | NA | NA | NA
29 | LOCATE ANY NEW IRRIGATION CONTROLLER AND COORDINATE AND PROVIDE POWER | NA | NA | NA
ASD101 DEMOLITION SITE PLAN
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA | NA
2 | SHOW DEMOLITION REQUIRED FOR EQUIPMENT RIGGING SCOPE AS COORDINATED WITH VENDOR/OWNER | NA | NA
3 | SHOW EXISTING PARKING | NA
4 | SHOW TREE DEMOLITION AND EXISTING TO REMAIN SCOPE AS COORDINATED WITH LANDSCAPE CONSULTANT | NA
5 | REVIEW CIVIL FOR GRADE OR UTILITY CONNECTION CHANGES | NA
6 | INDICATE DRAWING SCALE
G-001 COVER SHEET
1 | VERIFY PROJECT NAME MATCHES NAME ON CONTRACT | NA
2 | EDIT TO INCLUDE ALL CONSULTANTS ON PROJECT | NA | NA
3 | INCLUDE VICINITY MAP | NA
4 | INCLUDE CAMPUS MAP AND/OR BUILDING KEY PLAN IF REQUIRED | NA
5 | USE THE APPROPRIATE GRACE TITLEBLOCK FOR TEAM
6 | EDIT REVISIONS FPR ADDENDA/CHANGE DIRECTIVES | NA | NA | NA
7 | INCLUDE PROJECT IMAGE | NA
8 | INCLUDE AGENCY REVIEW NUMBER ON TITLESHEET WHEN APPLICABLE | NA | NA
G-010 SHEET INDEX & PROJECT INFO
1 | EDIT ALL GENERAL NOTES TO INCLUDE ONLY APPLICABLE NOTES | NA | NA | NA
2 | ENSURE SHEET LIST IS PROJECT SPECIFIC | NA | NA
3 | UPDATE CONSULTANT SHEET LISTS | NA | NA
4 | ENSURE DRAWINGS ARE LISTED IN ORDER OF AHJ PREFERENCE | NA | NA
5 | EDIT NOTES WITH PM: SUBMITTALS | SPECIAL INSPECTION AND BIDS | NA | NA
G-100 CODE INFORMATION
1 | DOCUMENT PROJECT DATA
2 | DOCUMENT BUILDING CODES AND GUIDELINES
3 | DOCUMENT EXISTING BUILDING DATA
4 | DOCUMENT NEW BUILDING DATA | NA
5 | DO OCCUPANCY CALCULATIONS | NA
6 | DO PLUMBING FIXTURE CALCULATIONS | NA
7 | IDENTIFY AND CONFIRM AHJ TITLBLOCK | SHEET NAMING / OTHER PERMIT SPECIFIC REQUIREMENTS | NA | NA
G-101 LIFE SAFETY PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES | NA | NA
2 | DOCUMENT RATED WALLS ON PLAN TO MATCH LEGEND AND UL LISTED ASSEMBLY | NA | NA | NA
3 | DOCUMENT ALL LIFE SAFETY ITEMS PER ANNOTATION LEGEND | NA | NA | NA
4 | LOCATE AND TAG FIRE ALARM ANNUNCIATOR PANEL | NA | NA | NA
5 | CONFIRM EXIT ACCESS AND COMMON PATH OF TRAVEL COMPLY WITH CODE | NA | NA
6 | LABEL ALL EXITS | NA | NA
7 | PROVIDE REQUIRED AND PROVIDED EXIT CAPACITY CALCULATIONS | NA | NA
8 | CHECK DEAD ENDS COMPLY WITH CODE
9 | SHOW THE ARCHITECTURAL LIMIT | NA
10 | ORGANIZE YOUR PLANS IN QUADRANTS/FLOORS AS REQUIRED | NA
11 | LOCATE EXIT SIGNAGE WITH DIRECTIONAL ARROWS | NA
12 | SHOW COLOR SCHEME TO MATCH FUNCTION OF SPACE | NA
13 | SHOW OCCUPANT LOAD OF ROOMS
14 | ENSURE PLOT AND LINE WEIGHTS ARE LEGIBLE | NA
15 | INDICATE FEC LOCATIONS
16 | SHOW MINIMUM SEPARATION DISTANCE BETWEEN EXITS
17 | INDICATE DRAWING SCALE
G-121 SMOKE COMPARTMENT PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES
2 | DOCUMENT SMOKE AND RATED SMOKE WALLS ON PLAN TO MATCH LEGEND AND UL LISTED ASSEMBLY
3 | SHOW COLOR SCHEME TO SHOW SMOKE COMPARTMENT LEGEND
4 | DOCUMENT ALL LIFE SAFETY ITEMS PER ANNOTATION LEGEND
5 | CONFIRM EXIT ACCESS AND COMMON PATH OF TRAVEL COMPLY WITH CODE
6 | LABEL ALL EXITS
7 | PROVIDE REQUIRED AND PROVIDED EXIT CAPACITY CALCULATIONS
8 | CHECK DEAD ENDS COMPLY WITH CODE
9 | SHOW THE ARCHITECTURAL LIMIT
10 | ORGANIZE YOUR PLANS IN QUADRANTS/FLOORS AS REQUIRED
11 | PROVIDE EXIT CALCULATION FOR EACH SMOKE COMPARTMENT
12 | LOCATE EXIT SIGNAGE WITH DIRECTIONAL ARROWS
13 | ENSURE PLOT AND LINE WEIGHTS ARE LEGIBLE
14 | INDICATE DRAWING SCALE
G-200 ACCESSIBILITY DETAILS
1 | ADD IN AHJ COMPLIANT ACCESSIBILITY DETAILS FROM CMS
2 | EDIT OUT CMS SHEETS THAT ARE NOT APPLICABLE
3 | SHOW ADA COMPLIANT TRANSITIONS FOR CHANGES IN LEVEL
4 | SHOW TURNING CIRCULAR AND T-SHAPED OUTLINES ON LIFE SAFETY/ENLARGED PLANS PER PM REQUIREMENT
5 | SHOW CLEAR FLOOR SPACE REQUIREMENTS AT SINKS AND WATER CLOSETS
6 | COMPLY WITH UNOBSTRUCTED AND OBSTRUCTED REACH RANGES FOR MILLWORK IN ELEVATION
7 | COMPLY WITH REQUIREMENTS FOR EQUIPMENT OPERABLE PARTS
8 | REVIEW PARALLEL AND FORWARD APPROACH MANEUVERING CLEARANCES AT COUNTERS AND EQUIPMENT
9 | SHOW KNEE AND TOE CLEARANCES IN MILLWORK SECTIONS
10 | IDENTIFY AND REVIEW PROTRUDING OBJECTS ON CIRCULATION PATHS
11 | IDENTIFY REDUCED VERTICAL CLEARANCE AREAS AND REVIEW WITH PM
12 | REVIEW WALKING SURFACES AT DOORS FOR CLEAR WIDTH OF ACCESSIBLE ROUTE
13 | REVIEW DOORS AND DOORWAYS FOR MANUAL SWINGING DOORS | SLIDING DOORS | RECESSED DOORS | DOORS IN A SERIES | DOORS WITH CLOSERS
14 | IDENTIFY AND REVIEW INTENTIONAL DEVIATIONS WITH PM AND REPORT TO STORYTELLER FOR PEER REVIEW
15 | VERIFY CH 11 REQUIREMENTS ARE COORDINATED (OR EQUAL JURISDICTION)
G-300 PARTITION DETAILS
1 | USE GRACE STANDARD PARTITION TYPES
2 | DETAIL ALL IN USE PARTITION TYPES
3 | DETAIL ALL UNIQUE TO PROJECT PARTITION TYPES
4 | EDIT NON-APPLICABLE GENERAL NOTES
5 | EDIT NON-APPLICABLE GENERAL NOTES | NA
6 | SHOW BASE AND HEAD CONDITION FOR ALL PARTITIONS | NA
7 | DETAIL RATED/UNRATED PARTITIONS AND STC RATING | NA
8 | SHOW COMPOSITE / NON COMPOSITE STUD SPACING FOR DEFLECTION | THICKNESS (GUAGE) | SIZE AND LIMITING HEIGHTS | NA
9 | DETAIL USE OF ACOUSTIC SOUND BATTS WHERE APPLICABLE | NA
10 | IDENTIFY AND DETAIL FOR SPECIAL USES: BALLISTIIC/LEAD | SECURITY MESH | ACOUSTIC ENHANCED GWB | CEMENT BOARD | MOISTURE AND MOLD RESISTANT GWB | NA
11 | ONLY DOCUMENT INTERIOR WALLS FOR PARTITON DETAILS; DOCUMENT EXTERIOR ENVELOPE IN THE BUILDING SECTIONS
12 | INDICATE DRAWING SCALE
G-501 LISTED ASSEMBLY DETAILS
1 | DOCUMENT RATED WALLS AND MATCH WITH LEGEND AND LIFE SAFETY PLAN
2 | DOCUMENT RATED CEILINGS
3 | DOCUMENT HORIZONTAL EXITS
4 | DOCUMENT RATED ROOFS
5 | DOCUMENT RATED FLOORS
6 | DOCUMENT ALL PENETRATIONS AT RATED ASSEMBLIES
7 | DOCUMENT FIRE RATED SEALANT IN SEALANT SCHEDULE AND NOTE FOR USE AT RATED WALLS OR FLOORS
ID101 FINISH PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES
2 | IF NOT USING THE FLOOR PATTERN PLAN AND THE WALL PROTECTION PLAN | THEN: SHOW ALL FINISHES ON THIS PLAN INCLUDING FLOOR FINISHES AND WALL PROTECTION; FLOOR FINISHES ARE TO TRANSITON AT THE CENTER OF DOORS WHERE POSSIBLE
3 | SHOW WALL FINISH EXTENTS
4 | SHOW ROOM FINISH TAG IN ALL ROOMS WITH NEW FINISH SCOPE
5 | IDENTY MILLWORK COUNTER TOP FINISHES IN PLAN AND NOTE THAT FLOOR FINISHES EXTEND UNDER MILLWORK
6 | WHEN SPECIFYING INTEGRAL BASE FOR EASIER CLEANING | ENSURE THE BASE COVE AREA DETAIL SHOWS A COVE STICK RADIUS PER THE VENDOR SPECIFICATION FOR EASE OF INSTALLATION
7 | WHEN SPECIFYING SANITARY BASE FOR EASIER CLEANING | ENSURE THE BASE IS NOTED TO BE CONTIGUOUS AT ROOM PERIMITER AND AROUND THE TOEKICKS OF MILLWORK
8 | IDENTIFY EXISTING FLOOR FINISHES TO REMAIN REQUIRING FLOOR TRANSTION DETAILING
9 | INDICATE DRAWING SCALE
ID111 FLOOR PATTERN PLANS
1 | SHOW FLOOR FINISH PATTERNS PER THE INTERIOR FINISH SYMBOL LEGEND
2 | TAG ALL FINISHES IN INTERIOR FINISH SYMBOL LEGEND TO MATCH SPECIFIED FINISHES
3 | INDICATE FLOOR FINISH PATTERN DIRECTION WITH AN ARROW
4 | INDICATE OVERHEAD CEILING DEIGN ELEMENTS FOR REFERENCE. PROVIDE 3D VIEWS AS REQUIRED BY TEAM FRO INTERNAL REVIEW
5 | INDICATE RESILIENT SHEET COLD/HEAT WELD LOCATIONS AND SPECIFY WELD COLOR
6 | INDICATE ALL FLOOR TRANSITIONS IN PLAN AND REFERENCE IN DETAILS
7 | INDICATE DRAWING SCALE
ID131 SIGNAGE PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES
2 | EDIT SIGNAGE FINISHES
3 | MATCH SIGN TAGS WITH INTERIORS SIGNAGE LEGEND
4 | LOCATE SIGNS IN COMPLIANCE WITH ADA AND LIFE SAFETY REQUIREMENTS
5 | USE INTERIOR SIGNAGE TYPES PER LOCATION: RESTROOMS | EXITS | ROOMS
6 | USE INTERIOR SIGNAGE TYPES PER LOW RISK OR HIGH RISK TYPES IN BEHAVIORAL HEALTH SPACES
7 | INDICATE DRAWING SCALE
ID141 WALL PROTECTION PLANS
1 | USE A WALL PROTECTION FAMILY THAT CAN BE READ AND TAGGED IN PLAN VIEW
2 | USE A WALL PROTECTION FAMILY THAT SHOWS THE WALL PROTECTION SCOPE IN ELEVATION
3 | COORDINATE WALL MOUNTED EQUIPMENT AT ALL WALL BUMPERS | CHAIR RAILS ETC
4 | COORDINATE DOOR SWINGS AND LEVER HARDWARE AT ALL WALL BUMPERS | CHAIR RAILS ETC
5 | REFERENCE WALL PROTECTION DETAILS AND NOTE WALL PROTECTION FINISHES/COLORS
6 | INDICATE DRAWING SCALE
ID151 FURNITURE PLANS
1 | EDIT NON-APPLICABLE GENERAL NOTES
2 | CLEARLY INDICATE WHAT FURNITURE SCOPE IS IN THE PROJECT BID SCOPE
3 | ENSURE FURNITURE AND EQUIPMENT CAN BE GRAPHICALLY UNDERSTOOD AS SEPARATE SCOPE ITEMS
4 | TAG ALL FURNITURE PER FURNITURE SPECIFICATIONS
5 | FOR POWERED FURNITURE | INDICATE POWER CONNECTION LOCATIONS AS COORDINATED WITH VENDOR
6 | INDICATE CRITICAL HOLD/CLEAR DIMENSIONS FOR FURNITURE WHEN TIGHT TO PARTITIONS
7 | COORDINATE CHAIR COUNTS WITH LIFE SAFETY PLAN AND PM
8 | INDICATE DRAWING SCALE
ID201 INTERIOR CASEWORK ELEVATIONS
1 | CONFIRM THE DESIGN TEAM'S STRATEGY FOR INTERIOR VS CASEWORK ELEVATIONS VIEW TITLES AND TEMPLATES
2 | SHOW MILLWORK AND REFERENCE DETAILS
3 | SHOW AND TAG WALL MOUNTED EQUIPMENT; DIMENSION LOCATION OF RECEPTACLES FOR RECPTACLES BEHIND EQUIPMENT PER PM DIRECTION.
4 | SHOW MEDICAL GAS
5 | SHOW MILLWORK COUNTERS AT 30"/34" ADA HT; SHOW AT NON ADA HEIGHT AS COORDINATED WITH PM PER SPECIFIC PROJECT REQUIREMENTS
6 | CONFIRM REQUIRED HEIGHT BETWEEN COUNTERTOP AND UPPER WALL MILLWORK IS 2'-0" OR OTHER | INCLUDING EQUIPMENT CLEARANCES.
7 | LOCATE AND TAG WALL PROTECTION/CORNER GUARDS AND REFERENCE DETAILS
8 | SHOW WHERE EXISTING FINISHES TRANSITION TO NEW FINISHES
9 | CONFIRM FINISHES MATCH OWNER DESIGN STANDARDS WHERE APPLICABLE
10 | CONFIRM MILLWORK TOEKICK HEIGHTS
11 | TAG WALL FINISHES AND ENSURE WALL (INTEGRAL/SANITARY OR OTHER) BASE HEIGHT SHOWN MATCHES FINISH LEGEND
12 | INDICATE DRAWING SCALE
ID301 FINISH DETAILS
1 | DETAIL BUILDING PERIMETER SOFFIT DETAIL AND INCLUDE BLINDS/ SUN SHADES /BLACKOUT SHADES
2 | DETAIL BUILDING PERIMETER BASE DETAIL AT MILLWORK OR PERIMTER HEATING
3 | DETAIL CEILING FINISHES
4 | DETAIL BULKHEAD DETAILS
5 | DETAIL WALL PROTECTION
6 | DETAIL FLOOR TRANSITIONS
7 | INDICATE DRAWING SCALE